## Sheet1
Drive HP = | 150 | Single Pump Scenarios
Drive kW(HP*0.7457)= | 111.855 | 100% Speed (No Drive) |  |  | Scenario 1 W/ Drive |  |  | Scenario 2 W/ Drive |  |  | Scenario 3 W/ Drive
Drive Package Cost($)= | 13000 | Run Time= | 8 | hr | Run Time= | 10 | hr | Run Time= | 11.4286 | hr | Run Time= | 13.3333 | hr
Electricity Cost($/kWh) | 0.06 | Speed= | 100 | % | Speed= | 80 | % | Speed= | 70 | % | Speed= | 60 | %
Cable Cost/ft ($/ft) | 5.3 | Power Consumption= | 1169.7255 | kWh | Power Consumption= | 788.0256 | kWh | Power Consumption= | 603.3321 | kWh | Power Consumption= | 443.2644 | kWh
Conduit Cost/ft ($/ft) | 19.2 |  |  |  | Less Power than 100%= | 32.6316 | % | Less Power than 100%= | 48.4211 | % | Less Power than 100%= | 62.1053 | %
Cable/Conduit Length (ft) | 50 | Cost Per Hour to Run= | 8.7729 | $/hr | Cost Per Hour to Run= | 4.7282 | $/hr | Cost Per Hour to Run= | 3.1675 | $/hr | Cost Per Hour to Run= | 1.9947 | $/hr
Labor Install Cost ($) | 1440 |  |  |  | Time to Payoff Drive | 3872.8857 | hours | Time to Payoff Drive | 2794.6028 | hours | Time to Payoff Drive | 2311.068 | hours
Total Cost of Drive ($) | 15665 |  |  |  | Days to Payoff Drive | 387.2886 | days | Days to Payoff Drive | 244.5277 | days | Days to Payoff Drive | 173.3301 | days
Avg run time per day(hr) | 8 |  |  |  | Years to Payoff Drive | 1.0611 | years | Years to Payoff Drive | 0.66994 | years | Years to Payoff Drive | 0.47488 | years
Additional Pump & Motor($) | 5000 | Other benefits not quantified
Pump Efficiency (%) | 85 | 1. VFDs eliminate the need for a soft start and give the benefit of reducing water hammer, saving equipment and piping integrity
Motor Efficiency (%) | 90 | 2. Pump Clean-Can automatically detect fouling of impellor and reverse to clear it
VFD Efficiency (%) | 95 | 3. Automatic detection of broken pipes
4. Under Load protection- detects if No flow or Pump is dry.
Pump Affinity Law Reference |  | 5. Power on Resume-If Power is lost drive will pick back up where it was running before loss of power
|  | 6. Separate Overload Protection not needed-Drive has overload protection built in | [8 empty] | Average Electrical Rates 2021 ($/kwh)
Drive Speed(%) | Power Consumption(%) | Single Pump Across line vs dual pumps with drives Scenarios | [9 empty] | Commercial | Industrial
100 | 100 | 100% Speed (No Drive)-Single Pump |  |  | Two Pumps with Drives Slower Speed | [5 empty] | Pittsburgh | 0.0372 | 0.0135
95 | 85.7375 | Run Time= | 8 | hr | Run Time= | 8 | hr |  |  |  | Cleveland | 0.1187 | 0.0073
90 | 72.9 | Speed= | 100 | % | Speed= | 68.7994 | % |  |  |  | Columbus | 0.113 | 0.0845
85 | 61.4125 | Power Consumption= | 1169.7255 | kWh | Power Consumption= | 801.9462 | kWh |  |  |  | Cincinnati | 0.0428 | 0.0139
80 | 51.2 |  |  |  | Less Power than 100%= | 31.4415 | % |  |  |  | Toledo | 0.0519 | 0.0155
75 | 42.1875 | Cost Per Hour to Run= | 8.7729 | $/hr | Cost Per Hour to Run= | 6.0146 | $/hr |  |  |  | Louisville | 0.0834 | 0.0617
70 | 34.3 |  |  |  | Time to Payoff Drive | 13170.943 | hours |  |  |  | Charleston WV | 0.0847 | 0.0649
65 | 27.4625 |  |  |  | Days to Payoff Drive | 1646.3679 | days |  |  |  | Orlando | 0.0938 | 0.0804
60 | 21.6 |  |  |  | Years to Payoff Drive | 4.5106 | years |  |  |  | Jacksonville | 0.128 | 0.0591
55 | 16.6375 | [9 empty] | Tampa | 0.1021 | 0.0884
50 | 12.5 | [9 empty] | Miami | 0.0872 | 0.0682
https://www.electricitylocal.com/